## FTA+ETA
F1-a1-1(t) | 充電電壓設定不當 | [14 empty] | 3-1-電芯未發生熱失控 | Impact 01 | 5-1-未發生電芯熱失控傳播現象 | Impact 02
[16 empty] | R003=75.2% ~ 83.2% | P(01)=35.75% | R006=71.6% ~ 79.1% | P(02)=2.374% |  |  |  | 10-1-熱煙或毒性氣體未危害至儲能空間以外 | Impact 05
11.1% |  | AND | F1-a1(t) | 充電電壓設定不當 | [12 empty] | 4-1-通風排出裝置啟動 |  | 6-1-未發生模組熱失控傳播現象 | Impact 03 |  |  | R014=70.0% ~ 77.3% | P(05)=0.011%
[17 empty] | R005=32.3% ~ 35.7% |  | R008=73.1% ~ 80.8% | P(03)=0.606% |  | 9-1-消防系統有效發揮冷卻作用
|  |  | 1.321% | [14 empty] | 5-2-發生電芯熱失控傳播現象 |  | 7-1-未發生電池櫃熱失控傳播現象 | Impact 04 | R013=65.2% ~ 72.1% | 10-2-熱煙或毒性氣體危害至儲能空間以外 | Impact 06
F1-a1-2(t) | 充電電壓控制器故障 | [16 empty] | R007=20.9% ~ 28.4% |  | R010=73.1% ~ 80.8% | P(04)=0.139% |  | R015=22.7% ~ 30.0% | P(06)=0.004%
[5 empty] | AND | [9 empty] | 2-1-BESS緊急安全關斷 | [5 empty] | 8-1-可燃氣體濃度未達到LFL
11.9% | [14 empty] | R002=68.1% ~ 75.2% |  |  |  | 6-2-發生模組熱失控傳播現象 |  | R012=49.2% ~ 54.4% |  | 10-3-熱煙或毒性氣體未危害至儲能空間以外 | Impact 07
[19 empty] | R009=19.2% ~ 26.9% |  |  |  | R017=56.0% ~ 61.9% | P(07)=0.004%
9-2-消防系統無法發揮冷卻作用
F1-a2-1(t) | 過電壓保護設定不當 | [20 empty] | R016=27.9% ~ 34.8% | 10-4-熱煙或毒性氣體危害至儲能空間以外 | Impact 08
[23 empty] | R018=38.1% ~ 44.0% | P(08)=0.003%
12.6% |  | AND | F1-a2(t) | 充電電壓設定不當 | [15 empty] | 7-2-發生電池櫃熱失控傳播現象
[16 empty] | 3-2-電芯發生熱失控 |  |  |  | R011=19.2% ~ 26.9% |  |  | 10-5-熱煙或毒性氣體未危害至儲能空間以外 | Impact 09
|  |  | 1.361% | [12 empty] | R004=16.8% ~ 24.8% | [6 empty] | R021=70.0% ~ 77.3% | P(09)=0.009%
F1-a2-2(t) | 過電壓保護裝置故障 | [20 empty] | 9-3-消防系統有效發揮冷卻作用
[22 empty] | R020=55.4% ~ 61.3% | 10-6-熱煙或毒性氣體危害至儲能空間以外 | Impact 10
10.8% | [22 empty] | R022=22.7% ~ 30.0% | P(10)=0.003%
8-2-可燃氣體濃度達到LFL
[21 empty] | R019=45.6% ~ 50.8% |  | 10-7-熱煙或毒性氣體未危害至儲能空間以外 | Impact 11
F1-b1-1(t) | 充電電流設定不當 | [21 empty] | R024=56.0% ~ 61.9% | P(11)=0.005%
9-4-消防系統無法發揮冷卻作用
10.85% |  | AND | F1-b1(t) | 充電電壓設定不當 | [17 empty] | R023=38.7% ~ 44.6% | 10-8-熱煙或毒性氣體危害至儲能空間以外 | Impact 12
[18 empty] | 5-3-未發生電芯熱失控傳播現象 | Impact 13 |  |  |  | R025=38.1% ~ 44.0% | P(12)=0.003%
|  |  | 1.291% | [14 empty] | R027=71.6% ~ 79.1% | P(13)=4.640%
F1-b1-2(t) | 充電電流控制器故障 | [15 empty] | 4-2-通風排出裝置未啟動 |  | 6-3-未發生模組熱失控傳播現象 | Impact 14 |  |  | 10-9-熱煙或毒性氣體未危害至儲能空間以外 | Impact 16
[5 empty] | AND | [11 empty] | R026=64.3% ~ 67.7% |  | R029=73.1% ~ 80.8% | P(14)=1.148% |  | 9-5-消防系統有效發揮冷卻作用 | R035=70.0% ~ 77.3% | P(16)=0.010%
11.9% | [17 empty] | 5-4-發生電芯熱失控傳播現象 |  | 7-3-未發生電池櫃熱失控傳播現象 | Impact 15 | R034=65.2% ~ 72.1%
[18 empty] | R028=20.9% ~ 28.4% |  | R031=73.1% ~ 80.8% | P(15)=0.260% |  | 10-10-熱煙或毒性氣體危害至儲能空間以外 | Impact 17
[21 empty] | 8-3-可燃氣體濃度未達到LFL |  | R036=22.7% ~ 30.0% | P(17)=0.004%
F1-b2-1(t) | 過電流保護設定不當 | [12 empty] | 1-1-值班室或EWCS通報電池異常 |  |  |  |  | 6-4-發生模組熱失控傳播現象 |  | R033=24.6% ~ 27.2%
[14 empty] | R001=59.9% ~ 66.2% |  |  |  |  | R030=19.2% ~ 26.9% |  |  |  | 10-11-熱煙或毒性氣體未危害至儲能空間以外 | Impact 18
12.6% |  | AND | F1-b2(t) | 充電電壓設定不當 | [18 empty] | R038=56.0% ~ 61.9% | P(18)=0.004%
9-6-消防系統無法發揮冷卻作用
|  |  | 1.285% | [16 empty] | 7-4-發生電池櫃熱失控傳播現象 |  | R037=27.9% ~ 34.8% | 10-12-熱煙或毒性氣體危害至儲能空間以外 | Impact 19
F1-b2-2(t) | 過電流保護裝置故障 | [18 empty] | R032=19.2% ~ 26.9% |  |  | R039=38.1% ~ 44.0% | P(19)=0.003%
10.2% | [22 empty] | 10-13-熱煙或毒性氣體未危害至儲能空間以外 | Impact 20
[22 empty] | 9-7-消防系統有效發揮冷卻作用 | R042=70.0% ~ 77.3% | P(20)=0.025%
R041=55.4% ~ 61.3%
F1-c1-1(t) | 充電上限設定不當 | [21 empty] | 10-14-熱煙或毒性氣體危害至儲能空間以外 | Impact 21
[21 empty] | 8-4-可燃氣體濃度達到LFL |  | R043=22.7% ~ 30.0% | P(21)=0.009%
10.85% |  | AND | F1-c1(t) | 充電電壓設定不當 | [16 empty] | R040=72.8% ~ 75.4%
[23 empty] | 10-15-熱煙或毒性氣體未危害至儲能空間以外 | Impact 22
|  |  | 1.291% | [19 empty] | R045=56.0% ~ 61.9% | P(22)=0.014%
F1-c1-2(t) | 充電上限控制器故障 | [20 empty] | 9-8-消防系統無法發揮冷卻作用
[5 empty] | AND | [16 empty] | R044=38.7% ~ 44.6% | 10-16-熱煙或毒性氣體危害至儲能空間以外 | Impact 23
16% | [15 empty] | 3-3-電芯未發生熱失控 | Impact 24 | 5-5-未發生電芯熱失控傳播現象 | Impact 25 |  |  |  | R046=38.1% ~ 44.0% | P(23)=0.010%
[16 empty] | R048=22.6% ~ 24.9% | P(24)=1.156% | R051=71.6% ~ 79.1% | P(25)=1.451%
[19 empty] | 6-5-未發生模組熱失控傳播現象 | Impact 26 |  |  | 10-17-熱煙或毒性氣體未危害至儲能空間以外 | Impact 28
F1-c2-1(t) | 過充電保護設定不當 | [15 empty] | 4-3-通風排出裝置啟動 |  | R053=59.0% ~ 65.2% | P(26)=0.496% |  | 9-9-消防系統有效發揮冷卻作用 | R059=70.0% ~ 77.3% | P(28)=0.013%
[17 empty] | R050=25.4% ~ 28.1% |  |  | 7-5-未發生電池櫃熱失控傳播現象 | Impact 27 | R058=65.2% ~ 72.1%
14.7% |  | AND | F1-c2(t) | 充電電壓設定不當 | [7 empty] | 頂層事件(Top Event ) | [5 empty] | 5-6-發生電芯熱失控傳播現象 |  | R055=73.1% ~ 80.8% | P(27)=0.184% |  | 10-18-熱煙或毒性氣體危害至儲能空間以外 | Impact 29
[8 empty] | 電芯內部溫度異常 |  | T1 | [7 empty] | R052=20.9% ~ 28.4% |  |  | 8-5-可燃氣體濃度未達到LFL |  | R060=22.7% ~ 30.0% | P(29)=0.005%
|  |  | 1.361% |  |  |  | F1(t) |  |  |  |  | 電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels |  |  | 2-2-BESS未緊急安全關斷 | [5 empty] | R057=49.2% ~ 54.4%
F1-c2-2(t) | 過充電保護裝置故障 |  |  |  |  | OR |  |  | AND |  | OR |  |  |  | R047=24.8% ~ 31.9% |  |  |  | 6-6-發生模組熱失控傳播現象 |  |  |  | 10-19-熱煙或毒性氣體未危害至儲能空間以外 | Impact 30
[7 empty] | 0.06943% |  |  | 0.002877% | [8 empty] | R054=34.8% ~ 41.0% |  |  |  | R062=56.0% ~ 61.9% | P(30)=0.005%
13.2% | [21 empty] | 9-10-消防系統無法發揮冷卻作用
[7 empty] | F2(t) | 溫度保護機制失效 |  | T2 | [11 empty] | R061=27.9% ~ 34.8% | 10-20-熱煙或毒性氣體危害至儲能空間以外 | Impact 31
[20 empty] | 7-6-發生電池櫃熱失控傳播現象 |  |  | R063=38.1% ~ 44.0% | P(31)=0.003%
F1-d1-1(t) | 充電下限設定不當 | [5 empty] | 1.095% |  |  | 1.29% | [9 empty] | R056=19.2% ~ 26.9%
[12 empty] | Freq.Ann (Annual Frequency) = | 1.29% |  |  | 3-4-電芯發生熱失控 | [6 empty] | 10-21-熱煙或毒性氣體未危害至儲能空間以外 | Impact 32
13.15% |  | AND | F1-d1(t) | 充電電壓設定不當 | [11 empty] | R049=75.1% ~ 77.4% | [5 empty] | 9-11-消防系統有效發揮冷卻作用 | R066=70.0% ~ 77.3% | P(32)=0.010%
[7 empty] | F2-a1(t) | 電芯內部溫度異常 | [13 empty] | R065=55.4% ~ 61.3%
|  |  | 1.232% | [19 empty] | 10-22-熱煙或毒性氣體危害至儲能空間以外 | Impact 33
F1-d1-2(t) | 充電下限控制器故障 | [5 empty] | 10.4% |  | AND | [11 empty] | 8-6-可燃氣體濃度達到LFL |  | R067=22.7% ~ 30.0% | P(33)=0.004%
[5 empty] | AND | [15 empty] | R064=45.6% ~ 50.8%
16% | [22 empty] | 10-23-熱煙或毒性氣體未危害至儲能空間以外 | Impact 34
[7 empty] | F2-a2(t) | 溫度保護機制失效 | [14 empty] | R069=56.0% ~ 61.9% | P(34)=0.006%
9-12-消防系統無法發揮冷卻作用
F1-d2-1(t) | 過放電保護設定不當 | [5 empty] | 12.4% | [14 empty] | R068=38.7% ~ 44.6% | 10-24-熱煙或毒性氣體危害至儲能空間以外 | Impact 35
[18 empty] | 5-7-未發生電芯熱失控傳播現象 | Impact 36 |  |  |  | R070=38.1% ~ 44.0% | P(35)=0.004%
14.7% |  | AND | F1-d2(t) | 充電電壓設定不當 | [13 empty] | R072=71.6% ~ 79.1% | P(36)=7.394%
[19 empty] | 6-7-未發生模組熱失控傳播現象 | Impact 37 |  |  | 10-25-熱煙或毒性氣體未危害至儲能空間以外 | Impact 39
|  |  | 1.404% | [13 empty] | 4-4-通風排出裝置未啟動 |  | R074=73.1% ~ 80.8% | P(37)=1.935% |  | 9-13-消防系統有效發揮冷卻作用 | R080=70.0% ~ 77.3% | P(39)=0.018%
F1-d2-2(t) | 過放電保護裝置故障 | [15 empty] | R071=71.9% ~ 74.6% |  |  | 7-7-未發生電池櫃熱失控傳播現象 | Impact 38 | R079=65.2% ~ 72.1%
[18 empty] | 5-8-發生電芯熱失控傳播現象 |  | R076=73.1% ~ 80.8% | P(38)=0.448% |  | 10-26-熱煙或毒性氣體危害至儲能空間以外 | Impact 40
13.2% | [17 empty] | R073=20.9% ~ 28.4% |  |  | 8-7-可燃氣體濃度未達到LFL |  | R081=22.7% ~ 30.0% | P(40)=0.006%
R078=24.6% ~ 27.2%
[19 empty] | 6-8-發生模組熱失控傳播現象 |  |  |  | 10-27-熱煙或毒性氣體未危害至儲能空間以外 | Impact 41
[19 empty] | R075=19.2% ~ 26.9% |  |  |  | R083=56.0% ~ 61.9% | P(41)=0.007%
9-14-消防系統無法發揮冷卻作用
|  |  | F1-e1(t) | 電芯內部電阻異常 | [17 empty] | R082=27.9% ~ 34.8% | 10-28-熱煙或毒性氣體危害至儲能空間以外 | Impact 42
[20 empty] | 7-8-發生電池櫃熱失控傳播現象 |  |  | R084=38.1% ~ 44.0% | P(42)=0.005%
|  |  | 11.9% | [16 empty] | R077=19.2% ~ 26.9%
[23 empty] | 10-29-熱煙或毒性氣體未危害至儲能空間以外 | Impact 43
[5 empty] | AND | [16 empty] | 9-15-消防系統有效發揮冷卻作用 | R087=70.0% ~ 77.3% | P(43)=0.043%
R086=55.4% ~ 61.3%
[23 empty] | 10-30-熱煙或毒性氣體危害至儲能空間以外 | Impact 44
|  |  | F1-e2(t) | 電池散熱裝置故障 | [16 empty] | 8-8-可燃氣體濃度達到LFL |  | R088=22.7% ~ 30.0% | P(44)=0.016%
R085=72.8% ~ 75.4%
|  |  | 9.2% | [19 empty] | 10-31-熱煙或毒性氣體未危害至儲能空間以外 | Impact 45
[23 empty] | R090=56.0% ~ 61.9% | P(45)=0.025%
9-16-消防系統無法發揮冷卻作用
[22 empty] | R089=38.7% ~ 44.6% | 10-32-熱煙或毒性氣體危害至儲能空間以外 | Impact 46
[16 empty] | 3-5-電芯未發生熱失控 | Impact 47 | 5-9-未發生電芯熱失控傳播現象 | Impact 48 |  |  |  | R091=38.1% ~ 44.0% | P(46)=0.017%
[16 empty] | R094=75.2% ~ 83.2% | P(47)=10.455% | R097=71.6% ~ 79.1% | P(48)=0.718%
[17 empty] | 4-5-通風排出裝置啟動 |  | 6-9-未發生模組熱失控傳播現象 | Impact 49 |  |  | 10-33-熱煙或毒性氣體未危害至儲能空間以外 | Impact 51
[17 empty] | R096=32.3% ~ 35.7% |  | R099=73.1% ~ 80.8% | P(49)=0.187% |  | 9-17-消防系統有效發揮冷卻作用 | R105=70.0% ~ 77.3% | P(51)=0.003%
[18 empty] | 5-10-發生電芯熱失控傳播現象 |  | 7-9-未發生電池櫃熱失控傳播現象 | Impact 50 | R104=65.2% ~ 72.1%
[18 empty] | R098=20.9% ~ 28.4% |  | R101=73.1% ~ 80.8% | P(50)=0.043% |  | 10-34-熱煙或毒性氣體危害至儲能空間以外 | Impact 52
[15 empty] | 2-3-BESS緊急安全關斷 | [5 empty] | 8-9-可燃氣體濃度未達到LFL |  | R106=22.7% ~ 30.0% | P(52)=0.001%
[15 empty] | R093=34.0% ~ 37.6% |  |  |  | 6-10-發生模組熱失控傳播現象 |  | R103=49.2% ~ 54.4%
[19 empty] | R100=19.2% ~ 26.9% |  |  |  | 10-35-熱煙或毒性氣體未危害至儲能空間以外 | Impact 53
[23 empty] | R108=56.0% ~ 61.9% | P(53)=0.001%
9-18-消防系統無法發揮冷卻作用
[20 empty] | 7-10-發生電池櫃熱失控傳播現象 |  | R107=27.9% ~ 34.8% | 10-36-熱煙或毒性氣體危害至儲能空間以外 | Impact 54
[20 empty] | R102=19.2% ~ 26.9% |  |  | R109=38.1% ~ 44.0% | P(54)=0.001%
3-6-電芯發生熱失控
[16 empty] | R095=16.8% ~ 24.8% | [6 empty] | 10-37-熱煙或毒性氣體未危害至儲能空間以外 | Impact 55
[22 empty] | 9-19-消防系統有效發揮冷卻作用 | R112=70.0% ~ 77.3% | P(55)=0.003%
R111=55.4% ~ 61.3%
[23 empty] | 10-38-熱煙或毒性氣體危害至儲能空間以外 | Impact 56
[21 empty] | 8-10-可燃氣體濃度達到LFL |  | R113=22.7% ~ 30.0% | P(56)=0.001%
R110=45.6% ~ 50.8%
[23 empty] | 10-39-熱煙或毒性氣體未危害至儲能空間以外 | Impact 57
[23 empty] | R115=56.0% ~ 61.9% | P(57)=0.001%
9-20-消防系統無法發揮冷卻作用
[22 empty] | R114=38.7% ~ 44.6% | 10-40-熱煙或毒性氣體危害至儲能空間以外 | Impact 58
[18 empty] | 5-11-未發生電芯熱失控傳播現象 | Impact 59 |  |  |  | R116=38.1% ~ 44.0% | P(58)=0.001%
[18 empty] | R118=71.6% ~ 79.1% | P(59)=1.394%
[17 empty] | 4-6-通風排出裝置未啟動 |  | 6-11-未發生模組熱失控傳播現象 | Impact 60 |  |  | 10-41-熱煙或毒性氣體未危害至儲能空間以外 | Impact 62
[17 empty] | R117=64.3% ~ 67.7% |  | R120=73.1% ~ 80.8% | P(60)=0.347% |  | 9-21-消防系統有效發揮冷卻作用 | R126=70.0% ~ 77.3% | P(62)=0.003%
[18 empty] | 5-12-發生電芯熱失控傳播現象 |  | 7-11-未發生電池櫃熱失控傳播現象 | Impact 61 | R125=65.2% ~ 72.1%
[14 empty] | 1-2-值班室或EWCS未通報電池異常 |  |  |  | R119=20.9% ~ 28.4% |  | R122=73.1% ~ 80.8% | P(61)=0.079% |  | 10-42-熱煙或毒性氣體危害至儲能空間以外 | Impact 63
[14 empty] | R092=33.8% ~ 40.1% | [6 empty] | 8-11-可燃氣體濃度未達到LFL |  | R127=22.7% ~ 30.0% | P(63)=0.001%
[19 empty] | 6-12-發生模組熱失控傳播現象 |  | R124=24.6% ~ 27.2%
[19 empty] | R121=19.2% ~ 26.9% |  |  |  | 10-43-熱煙或毒性氣體未危害至儲能空間以外 | Impact 64
[23 empty] | R129=56.0% ~ 61.9% | P(64)=0.001%
9-22-消防系統無法發揮冷卻作用
[20 empty] | 7-12-發生電池櫃熱失控傳播現象 |  | R128=27.9% ~ 34.8% | 10-44-熱煙或毒性氣體危害至儲能空間以外 | Impact 65
[20 empty] | R123=19.2% ~ 26.9% |  |  | R130=38.1% ~ 44.0% | P(65)=0.001%
[23 empty] | 10-45-熱煙或毒性氣體未危害至儲能空間以外 | Impact 66
[22 empty] | 9-23-消防系統有效發揮冷卻作用 | R133=70.0% ~ 77.3% | P(66)=0.008%
R132=55.4% ~ 61.3%
[23 empty] | 10-46-熱煙或毒性氣體危害至儲能空間以外 | Impact 67
[21 empty] | 8-12-可燃氣體濃度達到LFL |  | R134=22.7% ~ 30.0% | P(67)=0.003%
R131=72.8% ~ 75.4%
[23 empty] | 10-47-熱煙或毒性氣體未危害至儲能空間以外 | Impact 68
[23 empty] | R136=56.0% ~ 61.9% | P(68)=0.004%
9-24-消防系統無法發揮冷卻作用
[22 empty] | R135=38.7% ~ 44.6% | 10-48-熱煙或毒性氣體危害至儲能空間以外 | Impact 69
[16 empty] | 3-7-電芯未發生熱失控 | Impact 70 | 5-13-未發生電芯熱失控傳播現象 | Impact 71 |  |  |  | R137=38.1% ~ 44.0% | P(69)=0.003%
[16 empty] | R139=22.6% ~ 24.9% | P(70)=5.652% | R142=71.6% ~ 79.1% | P(71)=3.660%
[17 empty] | 4-7-通風排出裝置啟動 |  | 6-13-未發生模組熱失控傳播現象 | Impact 72 |  |  | 10-49-熱煙或毒性氣體未危害至儲能空間以外 | Impact 74
[17 empty] | R141=25.4% ~ 28.1% |  | R144=73.1% ~ 80.8% | P(72)=0.916% |  | 9-25-消防系統有效發揮冷卻作用 | R150=70.0% ~ 77.3% | P(74)=0.017%
[18 empty] | 5-14-發生電芯熱失控傳播現象 |  | 7-13-未發生電池櫃熱失控傳播現象 | Impact 73 | R149=65.2% ~ 72.1%
[18 empty] | R143=20.9% ~ 28.4% |  | R146=73.1% ~ 80.8% | P(73)=0.209% |  | 10-50-熱煙或毒性氣體危害至儲能空間以外 | Impact 75
[15 empty] | 2-4-BESS未緊急安全關斷 | [5 empty] | 8-13-可燃氣體濃度未達到LFL |  | R151=22.7% ~ 30.0% | P(75)=0.006%
[15 empty] | R138=62.4% ~ 66.0% |  |  |  | 6-14-發生模組熱失控傳播現象 |  | R148=49.2% ~ 54.4%
[19 empty] | R145=19.2% ~ 26.9% |  |  |  | 10-51-熱煙或毒性氣體未危害至儲能空間以外 | Impact 76
[23 empty] | R153=56.0% ~ 61.9% | P(76)=0.006%
9-26-消防系統無法發揮冷卻作用
[22 empty] | R152=27.9% ~ 34.8% | 10-52-熱煙或毒性氣體危害至儲能空間以外 | Impact 77
[20 empty] | 7-14-發生電池櫃熱失控傳播現象 |  |  | R154=38.1% ~ 44.0% | P(77)=0.004%
[16 empty] | 3-8-電芯發生熱失控 |  |  |  | R147=19.2% ~ 26.9%
[16 empty] | R140=62.4% ~ 66.0% | [6 empty] | 10-53-熱煙或毒性氣體未危害至儲能空間以外 | Impact 78
[22 empty] | 9-27-消防系統有效發揮冷卻作用 | R157=70.0% ~ 77.3% | P(78)=0.013%
R156=55.4% ~ 61.3%
[23 empty] | 10-54-熱煙或毒性氣體危害至儲能空間以外 | Impact 79
[21 empty] | 8-14-可燃氣體濃度達到LFL |  | R158=22.7% ~ 30.0% | P(79)=0.005%
R155=45.6% ~ 50.8%
[23 empty] | 10-55-熱煙或毒性氣體未危害至儲能空間以外 | Impact 80
[23 empty] | R160=56.0% ~ 61.9% | P(80)=0.007%
9-28消防系統無法發揮冷卻作用
[22 empty] | R159=38.7% ~ 44.6% | 10-56-熱煙或毒性氣體危害至儲能空間以外 | Impact 81
[18 empty] | 5-15-未發生電芯熱失控傳播現象 | Impact 82 |  |  |  | R161=38.1% ~ 44.0% | P(81)=0.005%
[18 empty] | R163=71.6% ~ 79.1% | P(82)=10.041%
[17 empty] | 4-8-通風排出裝置未啟動 |  | 6-15-未發生模組熱失控傳播現象 | Impact 83 |  |  | 10-57-熱煙或毒性氣體未危害至儲能空間以外 | Impact 85
[17 empty] | R162=71.9% ~ 74.6% |  | R165=73.1% ~ 80.8% | P(83)=2.540% |  | 9-29-消防系統有效發揮冷卻作用 | R171=70.0% ~ 77.3% | P(85)=0.045%
[18 empty] | 5-16-發生電芯熱失控傳播現象 |  | 7-15-未發生電池櫃熱失控傳播現象 | Impact 84 | R170=65.2% ~ 72.1%
[18 empty] | R164=20.9% ~ 28.4% |  | R167=73.1% ~ 80.8% | P(84)=0.576% |  | 10-58-熱煙或毒性氣體危害至儲能空間以外 | Impact 86
[21 empty] | 8-15-可燃氣體濃度未達到LFL |  | R172=22.7% ~ 30.0% | P(86)=0.016%
[19 empty] | 6-16-發生模組熱失控傳播現象 |  | R169=24.6% ~ 27.2%
[19 empty] | R166=19.2% ~ 26.9% |  |  |  | 10-59-熱煙或毒性氣體未危害至儲能空間以外 | Impact 87
[23 empty] | R174=56.0% ~ 61.9% | P(87)=0.016%
9-30-消防系統無法發揮冷卻作用
[20 empty] | 7-16-發生電池櫃熱失控傳播現象 |  | R173=27.9% ~ 34.8% | 10-60-熱煙或毒性氣體危害至儲能空間以外 | Impact 88
[20 empty] | R168=19.2% ~ 26.9% |  |  | R175=38.1% ~ 44.0% | P(88)=0.011%
[23 empty] | 10-61-熱煙或毒性氣體未危害至儲能空間以外 | Impact 89
[22 empty] | 9-31-消防系統有效發揮冷卻作用 | R178=70.0% ~ 77.3% | P(89)=0.035%
R177=55.4% ~ 61.3%
[23 empty] | 10-62-熱煙或毒性氣體危害至儲能空間以外 | Impact 90
[21 empty] | 8-16-可燃氣體濃度達到LFL |  | R179=22.7% ~ 30.0% | P(90)=0.013%
R176=72.8% ~ 75.4%
[23 empty] | 10-63-熱煙或毒性氣體未危害至儲能空間以外 | Impact 91
[23 empty] | R181=56.0% ~ 61.9% | P(91)=0.020%
9-32-消防系統無法發揮冷卻作用
[22 empty] | R180=38.7% ~ 44.6% | 10-64-熱煙或毒性氣體危害至儲能空間以外 | Impact 92
[23 empty] | R182=38.1% ~ 44.0% | P(92)=0.014%

## D01
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常
R001=59.9% ~ 66.2%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
Freq.Ann (Annual Frequency)
1-2-值班室或EWCS未通報電池異常
R092=45.8% ~ 51.0%

## D02
2-1-BESS緊急安全關斷
R002=68.1% ~ 75.2%
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常
R001=59.9% ~ 66.2%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
Freq.Ann (Annual Frequency)
2-2-BESS未緊急安全關斷
R047=24.8% ~ 31.9%

## D03
|  |  | 3-1-電芯未發生熱失控 | Impact 01
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75%
2-1-BESS緊急安全關斷
R002=68.1% ~ 75.2%
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常
R001=59.9% ~ 66.2%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
3-2-電芯發生熱失控
Freq.Ann (Annual Frequency) |  |  | R004=16.8% ~ 24.8%

## D04
|  |  | 3-1-電芯未發生熱失控 | Impact 01
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75%
4-1-通風排出裝置啟動
R005=32.3% ~ 35.7%
2-1-BESS緊急安全關斷
R002=68.1% ~ 75.2%
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常
R001=59.9% ~ 66.2%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
3-2-電芯發生熱失控
Freq.Ann (Annual Frequency) |  |  | R004=16.8% ~ 24.8%
4-2-通風排出裝置未啟動
R026=64.3% ~ 67.7%

## D05
|  |  | 3-1-電芯未發生熱失控 | Impact 01 | 5-1-未發生電芯熱失控傳播現象 | Impact 02
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75% | R006=71.6% ~ 79.1% | P(02)=2.374%
4-1-通風排出裝置啟動
R005=32.3% ~ 35.7%
5-2-發生電芯熱失控傳播現象
R007=20.9% ~ 28.4%
2-1-BESS緊急安全關斷
R002=68.1% ~ 75.2%
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常
R001=59.9% ~ 66.2%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
3-2-電芯發生熱失控
Freq.Ann (Annual Frequency) |  |  | R004=16.8% ~ 24.8%
[5 empty] | 5-3-未發生電芯熱失控傳播現象 | Impact 13
[5 empty] | R027=71.6% ~ 79.1% | P(13)=4.640%
4-2-通風排出裝置未啟動
R026=64.3% ~ 67.7%
5-4-發生電芯熱失控傳播現象
R028=20.9% ~ 28.4%

## D06
|  |  | 3-1-電芯未發生熱失控 | Impact 01 | 5-1-未發生電芯熱失控傳播現象 | Impact 02
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75% | R006=71.6% ~ 79.1% | P(02)=2.374%
|  |  |  | 4-1-通風排出裝置啟動 |  | 6-1-未發生模組熱失控傳播現象 | Impact 03
|  |  |  | R005=32.3% ~ 35.7% |  | R008=73.1% ~ 80.8% | P(03)=0.606%
5-2-發生電芯熱失控傳播現象
R007=20.9% ~ 28.4%
2-1-BESS緊急安全關斷
|  | R002=68.1% ~ 75.2% |  |  |  | 6-2-發生模組熱失控傳播現象
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常 |  |  |  |  | R009=19.2% ~ 26.9%
R001=59.9% ~ 66.2%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
3-2-電芯發生熱失控
Freq.Ann (Annual Frequency) |  |  | R004=16.8% ~ 24.8%
[5 empty] | 5-3-未發生電芯熱失控傳播現象 | Impact 13
[5 empty] | R027=71.6% ~ 79.1% | P(13)=4.640%
|  |  |  | 4-2-通風排出裝置未啟動 |  | 6-3-未發生模組熱失控傳播現象 | Impact 14
|  |  |  | R026=64.3% ~ 67.7% |  | R029=73.1% ~ 80.8% | P(14)=1.148%
5-4-發生電芯熱失控傳播現象
R028=20.9% ~ 28.4%
6-4-發生模組熱失控傳播現象
R030=19.2% ~ 26.9%

## D07
|  |  | 3-1-電芯未發生熱失控 | Impact 01 | 5-1-未發生電芯熱失控傳播現象 | Impact 02
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75% | R006=71.6% ~ 79.1% | P(02)=2.374%
|  |  |  | 4-1-通風排出裝置啟動 |  | 6-1-未發生模組熱失控傳播現象 | Impact 03
|  |  |  | R005=32.3% ~ 35.7% |  | R008=73.1% ~ 80.8% | P(03)=0.606%
[5 empty] | 5-2-發生電芯熱失控傳播現象 |  | 7-1-未發生電池櫃熱失控傳播現象 | Impact 04
[5 empty] | R007=20.9% ~ 28.4% |  | R010=73.1% ~ 80.8% | P(04)=0.139%
2-1-BESS緊急安全關斷
|  | R002=68.1% ~ 75.2% |  |  |  | 6-2-發生模組熱失控傳播現象
R009=19.2% ~ 26.9%
7-2-發生電池櫃熱失控傳播現象
|  |  | 3-2-電芯發生熱失控 |  |  |  | R011=19.2% ~ 26.9%
R004=16.8% ~ 24.8%
[5 empty] | 5-3-未發生電芯熱失控傳播現象 | Impact 13
[5 empty] | R027=71.6% ~ 79.1% | P(13)=4.640%
|  |  |  | 4-2-通風排出裝置未啟動 |  | 6-3-未發生模組熱失控傳播現象 | Impact 14
|  |  |  | R026=64.3% ~ 67.7% |  | R029=73.1% ~ 80.8% | P(14)=1.148%
[5 empty] | 5-4-發生電芯熱失控傳播現象 |  | 7-3-未發生電池櫃熱失控傳播現象 | Impact 15
[5 empty] | R028=20.9% ~ 28.4% |  | R031=73.1% ~ 80.8% | P(15)=0.260%
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常 |  |  |  |  | 6-4-發生模組熱失控傳播現象
| R001=59.9% ~ 66.2% |  |  |  |  | R030=19.2% ~ 26.9%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
7-4-發生電池櫃熱失控傳播現象
R032=19.2% ~ 26.9%
Freq.Ann (Annual Frequency)

## D08
|  |  | 3-1-電芯未發生熱失控 | Impact 01 | 5-1-未發生電芯熱失控傳播現象 | Impact 02
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75% | R006=71.6% ~ 79.1% | P(02)=2.374%
|  |  |  | 4-1-通風排出裝置啟動 |  | 6-1-未發生模組熱失控傳播現象 | Impact 03
|  |  |  | R005=32.3% ~ 35.7% |  | R008=73.1% ~ 80.8% | P(03)=0.606%
[5 empty] | 5-2-發生電芯熱失控傳播現象 |  | 7-1-未發生電池櫃熱失控傳播現象 | Impact 04
[5 empty] | R007=20.9% ~ 28.4% |  | R010=73.1% ~ 80.8% | P(04)=0.139%
|  | 2-1-BESS緊急安全關斷 | [5 empty] | 8-1-可燃氣體濃度未達到LFL
|  | R002=68.1% ~ 75.2% |  |  |  | 6-2-發生模組熱失控傳播現象 |  | R012=49.2% ~ 54.4%
R009=19.2% ~ 26.9%
7-2-發生電池櫃熱失控傳播現象
|  |  | 3-2-電芯發生熱失控 |  |  |  | R011=19.2% ~ 26.9%
R004=16.8% ~ 24.8%
8-2-可燃氣體濃度達到LFL
R019=45.6% ~ 50.8%
[5 empty] | 5-3-未發生電芯熱失控傳播現象 | Impact 13
[5 empty] | R027=71.6% ~ 79.1% | P(13)=4.640%
|  |  |  | 4-2-通風排出裝置未啟動 |  | 6-3-未發生模組熱失控傳播現象 | Impact 14
|  |  |  | R026=64.3% ~ 67.7% |  | R029=73.1% ~ 80.8% | P(14)=1.148%
[5 empty] | 5-4-發生電芯熱失控傳播現象 |  | 7-3-未發生電池櫃熱失控傳播現象 | Impact 15
[5 empty] | R028=20.9% ~ 28.4% |  | R031=73.1% ~ 80.8% | P(15)=0.260%
8-3-可燃氣體濃度未達到LFL
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常 |  |  |  |  | 6-4-發生模組熱失控傳播現象 |  | R033=24.6% ~ 27.2%
| R001=59.9% ~ 66.2% |  |  |  |  | R030=19.2% ~ 26.9%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
7-4-發生電池櫃熱失控傳播現象
R032=19.2% ~ 26.9%
Freq.Ann (Annual Frequency)
8-4-可燃氣體濃度達到LFL
R040=72.8% ~ 75.4%

## D09
|  |  | 3-1-電芯未發生熱失控 | Impact 01 | 5-1-未發生電芯熱失控傳播現象 | Impact 02
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75% | R006=71.6% ~ 79.1% | P(02)=2.374%
|  |  |  | 4-1-通風排出裝置啟動 |  | 6-1-未發生模組熱失控傳播現象 | Impact 03
|  |  |  | R005=32.3% ~ 35.7% |  | R008=73.1% ~ 80.8% | P(03)=0.606% |  | 9-1-消防系統有效發揮冷卻作用
[5 empty] | 5-2-發生電芯熱失控傳播現象 |  | 7-1-未發生電池櫃熱失控傳播現象 | Impact 04 | R013=65.2% ~ 72.1%
[5 empty] | R007=20.9% ~ 28.4% |  | R010=73.1% ~ 80.8% | P(04)=0.139%
|  | 2-1-BESS緊急安全關斷 | [5 empty] | 8-1-可燃氣體濃度未達到LFL
|  | R002=68.1% ~ 75.2% |  |  |  | 6-2-發生模組熱失控傳播現象 |  | R012=49.2% ~ 54.4%
R009=19.2% ~ 26.9%
9-2-消防系統無法發揮冷卻作用
R016=27.9% ~ 34.8%
7-2-發生電池櫃熱失控傳播現象
|  |  | 3-2-電芯發生熱失控 |  |  |  | R011=19.2% ~ 26.9%
R004=16.8% ~ 24.8%
9-3-消防系統有效發揮冷卻作用
R020=55.4% ~ 61.3%
8-2-可燃氣體濃度達到LFL
R019=45.6% ~ 50.8%
9-4-消防系統無法發揮冷卻作用
R023=38.7% ~ 44.6%
[5 empty] | 5-3-未發生電芯熱失控傳播現象 | Impact 13
[5 empty] | R027=71.6% ~ 79.1% | P(13)=4.640%
|  |  |  | 4-2-通風排出裝置未啟動 |  | 6-3-未發生模組熱失控傳播現象 | Impact 14
|  |  |  | R026=64.3% ~ 67.7% |  | R029=73.1% ~ 80.8% | P(14)=1.148% |  | 9-5-消防系統有效發揮冷卻作用
[5 empty] | 5-4-發生電芯熱失控傳播現象 |  | 7-3-未發生電池櫃熱失控傳播現象 | Impact 15 | R034=65.2% ~ 72.1%
[5 empty] | R028=20.9% ~ 28.4% |  | R031=73.1% ~ 80.8% | P(15)=0.260%
8-3-可燃氣體濃度未達到LFL
頂層事件(Top Event ) | 1-1-值班室或EWCS通報電池異常 |  |  |  |  | 6-4-發生模組熱失控傳播現象 |  | R033=24.6% ~ 27.2%
| R001=59.9% ~ 66.2% |  |  |  |  | R030=19.2% ~ 26.9%
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
9-6-消防系統無法發揮冷卻作用
[7 empty] | 7-4-發生電池櫃熱失控傳播現象 |  | R037=27.9% ~ 34.8%
R032=19.2% ~ 26.9%
Freq.Ann (Annual Frequency)
9-7-消防系統有效發揮冷卻作用
R041=55.4% ~ 61.3%
8-4-可燃氣體濃度達到LFL
R040=72.8% ~ 75.4%
9-8-消防系統無法發揮冷卻作用
R044=38.7% ~ 44.6%

## D10
|  |  | 3-1-電芯未發生熱失控 | Impact 01 | 5-1-未發生電芯熱失控傳播現象 | Impact 02
|  |  | R003=75.2% ~ 83.2% | P(01)=35.75% | R006=71.6% ~ 79.1% | P(02)=2.374% |  |  |  | 10-1-熱煙或毒性氣體未危害至儲能空間以外 | Impact 05
|  |  |  | 4-1-通風排出裝置啟動 |  | 6-1-未發生模組熱失控傳播現象 | Impact 03 |  |  | R014=70.0% ~ 77.3% | P(05)=0.011%
|  |  |  | R005=32.3% ~ 35.7% |  | R008=73.1% ~ 80.8% | P(03)=0.606% |  | 9-1-消防系統有效發揮冷卻作用
[5 empty] | 5-2-發生電芯熱失控傳播現象 |  | 7-1-未發生電池櫃熱失控傳播現象 | Impact 04 | R013=65.2% ~ 72.1% | 10-2-熱煙或毒性氣體危害至儲能空間以外 | Impact 06
[5 empty] | R007=20.9% ~ 28.4% |  | R010=73.1% ~ 80.8% | P(04)=0.139% |  | R015=22.7% ~ 30.0% | P(06)=0.004%
|  | 2-1-BESS緊急安全關斷 | [5 empty] | 8-1-可燃氣體濃度未達到LFL
|  | R002=68.1% ~ 75.2% |  |  |  | 6-2-發生模組熱失控傳播現象 |  | R012=49.2% ~ 54.4% |  | 10-3-熱煙或毒性氣體未危害至儲能空間以外 | Impact 07
[6 empty] | R009=19.2% ~ 26.9% |  |  |  | R017=56.0% ~ 61.9% | P(07)=0.004%
9-2-消防系統無法發揮冷卻作用
[9 empty] | R016=27.9% ~ 34.8% | 10-4-熱煙或毒性氣體危害至儲能空間以外 | Impact 08
[10 empty] | R018=38.1% ~ 44.0% | P(08)=0.003%
7-2-發生電池櫃熱失控傳播現象
|  |  | 3-2-電芯發生熱失控 |  |  |  | R011=19.2% ~ 26.9% |  |  | 10-5-熱煙或毒性氣體未危害至儲能空間以外 | Impact 09
|  |  | R004=16.8% ~ 24.8% | [6 empty] | R021=70.0% ~ 77.3% | P(09)=0.009%
9-3-消防系統有效發揮冷卻作用
[9 empty] | R020=55.4% ~ 61.3% | 10-6-熱煙或毒性氣體危害至儲能空間以外 | Impact 10
[10 empty] | R022=22.7% ~ 30.0% | P(10)=0.003%
8-2-可燃氣體濃度達到LFL
[8 empty] | R019=45.6% ~ 50.8% |  | 10-7-熱煙或毒性氣體未危害至儲能空間以外 | Impact 11
[10 empty] | R024=56.0% ~ 61.9% | P(11)=0.005%
9-4-消防系統無法發揮冷卻作用
[9 empty] | R023=38.7% ~ 44.6% | 10-8-熱煙或毒性氣體危害至儲能空間以外 | Impact 12
[5 empty] | 5-3-未發生電芯熱失控傳播現象 | Impact 13 |  |  |  | R025=38.1% ~ 44.0% | P(12)=0.003%
[5 empty] | R027=71.6% ~ 79.1% | P(13)=4.640%
|  |  |  | 4-2-通風排出裝置未啟動 |  | 6-3-未發生模組熱失控傳播現象 | Impact 14 |  |  | 10-9-熱煙或毒性氣體未危害至儲能空間以外 | Impact 16
|  |  |  | R026=64.3% ~ 67.7% |  | R029=73.1% ~ 80.8% | P(14)=1.148% |  | 9-5-消防系統有效發揮冷卻作用 | R035=70.0% ~ 77.3% | P(16)=0.010%
[5 empty] | 5-4-發生電芯熱失控傳播現象 |  | 7-3-未發生電池櫃熱失控傳播現象 | Impact 15 | R034=65.2% ~ 72.1%
[5 empty] | R028=20.9% ~ 28.4% |  | R031=73.1% ~ 80.8% | P(15)=0.260% |  | 10-10-熱煙或毒性氣體危害至儲能空間以外 | Impact 17
[8 empty] | 8-3-可燃氣體濃度未達到LFL |  | R036=22.7% ~ 30.0% | P(17)=0.004%
| 1-1-值班室或EWCS通報電池異常 |  |  |  |  | 6-4-發生模組熱失控傳播現象 |  | R033=24.6% ~ 27.2%
| R001=59.9% ~ 66.2% |  |  |  |  | R030=19.2% ~ 26.9% |  |  |  | 10-11-熱煙或毒性氣體未危害至儲能空間以外 | Impact 18
[10 empty] | R038=56.0% ~ 61.9% | P(18)=0.004%
9-6-消防系統無法發揮冷卻作用
[7 empty] | 7-4-發生電池櫃熱失控傳播現象 |  | R037=27.9% ~ 34.8% | 10-12-熱煙或毒性氣體危害至儲能空間以外 | Impact 19
[7 empty] | R032=19.2% ~ 26.9% |  |  | R039=38.1% ~ 44.0% | P(19)=0.003%
[10 empty] | 10-13-熱煙或毒性氣體未危害至儲能空間以外 | Impact 20
[9 empty] | 9-7-消防系統有效發揮冷卻作用 | R042=70.0% ~ 77.3% | P(20)=0.025%
R041=55.4% ~ 61.3%
[10 empty] | 10-14-熱煙或毒性氣體危害至儲能空間以外 | Impact 21
[8 empty] | 8-4-可燃氣體濃度達到LFL |  | R043=22.7% ~ 30.0% | P(21)=0.009%
R040=72.8% ~ 75.4%
[10 empty] | 10-15-熱煙或毒性氣體未危害至儲能空間以外 | Impact 22
[10 empty] | R045=56.0% ~ 61.9% | P(22)=0.014%
9-8-消防系統無法發揮冷卻作用
[9 empty] | R044=38.7% ~ 44.6% | 10-16-熱煙或毒性氣體危害至儲能空間以外 | Impact 23
|  |  | 3-3-電芯未發生熱失控 | Impact 24 | 5-5-未發生電芯熱失控傳播現象 | Impact 25 |  |  |  | R046=38.1% ~ 44.0% | P(23)=0.010%
|  |  | R048=22.6% ~ 24.9% | P(24)=4.237% | R051=71.6% ~ 79.1% | P(25)=2.745%
[6 empty] | 6-5-未發生模組熱失控傳播現象 | Impact 26 |  |  | 10-17-熱煙或毒性氣體未危害至儲能空間以外 | Impact 28
|  |  |  | 4-3-通風排出裝置啟動 |  | R053=73.1% ~ 80.8% | P(26)=0.685% |  | 9-9-消防系統有效發揮冷卻作用 | R059=70.0% ~ 77.3% | P(28)=0.013%
|  |  |  | R050=25.4% ~ 28.1% |  |  | 7-5-未發生電池櫃熱失控傳播現象 | Impact 27 | R058=65.2% ~ 72.1%
[5 empty] | 5-6-發生電芯熱失控傳播現象 |  | R055=73.1% ~ 80.8% | P(27)=0.163% |  | 10-18-熱煙或毒性氣體危害至儲能空間以外 | Impact 29
[5 empty] | R052=20.9% ~ 28.4% |  |  | 8-5-可燃氣體濃度未達到LFL |  | R060=22.7% ~ 30.0% | P(29)=0.005%
|  | 2-2-BESS未緊急安全關斷 | [5 empty] | R057=49.2% ~ 54.4%
|  | R047=24.8% ~ 31.9% |  |  |  | 6-6-發生模組熱失控傳播現象 |  |  |  | 10-19-熱煙或毒性氣體未危害至儲能空間以外 | Impact 30
[6 empty] | R054=19.2% ~ 26.9% |  |  |  | R062=56.0% ~ 61.9% | P(30)=0.005%
9-10-消防系統無法發揮冷卻作用
[9 empty] | R061=27.9% ~ 34.8% | 10-20-熱煙或毒性氣體危害至儲能空間以外 | Impact 31
[7 empty] | 7-6-發生電池櫃熱失控傳播現象 |  |  | R063=38.1% ~ 44.0% | P(31)=0.003%
R056=19.2% ~ 26.9%
|  |  | 3-4-電芯發生熱失控 | [6 empty] | 10-21-熱煙或毒性氣體未危害至儲能空間以外 | Impact 32
|  |  | R049=75.1% ~ 77.4% | [5 empty] | 9-11-消防系統有效發揮冷卻作用 | R066=70.0% ~ 77.3% | P(32)=0.010%
R065=55.4% ~ 61.3%
[10 empty] | 10-22-熱煙或毒性氣體危害至儲能空間以外 | Impact 33
[8 empty] | 8-6-可燃氣體濃度達到LFL |  | R067=22.7% ~ 30.0% | P(33)=0.004%
R064=45.6% ~ 50.8%
[10 empty] | 10-23-熱煙或毒性氣體未危害至儲能空間以外 | Impact 34
[10 empty] | R069=56.0% ~ 61.9% | P(34)=0.006%
9-12-消防系統無法發揮冷卻作用
[9 empty] | R068=38.7% ~ 44.6% | 10-24-熱煙或毒性氣體危害至儲能空間以外 | Impact 35
[5 empty] | 5-7-未發生電芯熱失控傳播現象 | Impact 36 |  |  |  | R070=38.1% ~ 44.0% | P(35)=0.004%
[5 empty] | R072=71.6% ~ 79.1% | P(36)=7.394%
[6 empty] | 6-7-未發生模組熱失控傳播現象 | Impact 37 |  |  | 10-25-熱煙或毒性氣體未危害至儲能空間以外 | Impact 39
|  |  |  | 4-4-通風排出裝置未啟動 |  | R074=73.1% ~ 80.8% | P(37)=1.935% |  | 9-13-消防系統有效發揮冷卻作用 | R080=70.0% ~ 77.3% | P(39)=0.018%
頂層事件(Top Event ) |  |  |  | R071=71.9% ~ 74.6% |  |  | 7-7-未發生電池櫃熱失控傳播現象 | Impact 38 | R079=65.2% ~ 72.1%
[5 empty] | 5-8-發生電芯熱失控傳播現象 |  | R076=73.1% ~ 80.8% | P(38)=0.448% |  | 10-26-熱煙或毒性氣體危害至儲能空間以外 | Impact 40
電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels |  |  |  |  | R073=20.9% ~ 28.4% |  |  | 8-7-可燃氣體濃度未達到LFL |  | R081=22.7% ~ 30.0% | P(40)=0.006%
R078=24.6% ~ 27.2%
[6 empty] | 6-8-發生模組熱失控傳播現象 |  |  |  | 10-27-熱煙或毒性氣體未危害至儲能空間以外 | Impact 41
[6 empty] | R075=19.2% ~ 26.9% |  |  |  | R083=56.0% ~ 61.9% | P(41)=0.007%
Freq.Ann (Annual Frequency) | [8 empty] | 9-14-消防系統無法發揮冷卻作用
[9 empty] | R082=27.9% ~ 34.8% | 10-28-熱煙或毒性氣體危害至儲能空間以外 | Impact 42
[7 empty] | 7-8-發生電池櫃熱失控傳播現象 |  |  | R084=38.1% ~ 44.0% | P(42)=0.005%
R077=19.2% ~ 26.9%
[10 empty] | 10-29-熱煙或毒性氣體未危害至儲能空間以外 | Impact 43
[9 empty] | 9-15-消防系統有效發揮冷卻作用 | R087=70.0% ~ 77.3% | P(43)=0.043%
R086=55.4% ~ 61.3%
[10 empty] | 10-30-熱煙或毒性氣體危害至儲能空間以外 | Impact 44
[8 empty] | 8-8-可燃氣體濃度達到LFL |  | R088=22.7% ~ 30.0% | P(44)=0.016%
R085=72.8% ~ 75.4%
[10 empty] | 10-31-熱煙或毒性氣體未危害至儲能空間以外 | Impact 45
[10 empty] | R090=56.0% ~ 61.9% | P(45)=0.025%
9-16-消防系統無法發揮冷卻作用
[9 empty] | R089=38.7% ~ 44.6% | 10-32-熱煙或毒性氣體危害至儲能空間以外 | Impact 46
|  |  | 3-5-電芯未發生熱失控 | Impact 47 | 5-9-未發生電芯熱失控傳播現象 | Impact 48 |  |  |  | R091=38.1% ~ 44.0% | P(46)=0.017%
|  |  | R094=75.2% ~ 83.2% | P(47)=10.455% | R097=71.6% ~ 79.1% | P(48)=0.718%
|  |  |  | 4-5-通風排出裝置啟動 |  | 6-9-未發生模組熱失控傳播現象 | Impact 49 |  |  | 10-33-熱煙或毒性氣體未危害至儲能空間以外 | Impact 51
|  |  |  | R096=32.3% ~ 35.7% |  | R099=73.1% ~ 80.8% | P(49)=0.187% |  | 9-17-消防系統有效發揮冷卻作用 | R105=70.0% ~ 77.3% | P(51)=0.003%
[5 empty] | 5-10-發生電芯熱失控傳播現象 |  | 7-9-未發生電池櫃熱失控傳播現象 | Impact 50 | R104=65.2% ~ 72.1%
[5 empty] | R098=20.9% ~ 28.4% |  | R101=73.1% ~ 80.8% | P(50)=0.043% |  | 10-34-熱煙或毒性氣體危害至儲能空間以外 | Impact 52
|  | 2-3-BESS緊急安全關斷 | [5 empty] | 8-9-可燃氣體濃度未達到LFL |  | R106=22.7% ~ 30.0% | P(52)=0.001%
|  | R093=34.0% ~ 37.6% |  |  |  | 6-10-發生模組熱失控傳播現象 |  | R103=49.2% ~ 54.4%
[6 empty] | R100=19.2% ~ 26.9% |  |  |  | 10-35-熱煙或毒性氣體未危害至儲能空間以外 | Impact 53
[10 empty] | R108=56.0% ~ 61.9% | P(53)=0.001%
9-18-消防系統無法發揮冷卻作用
[7 empty] | 7-10-發生電池櫃熱失控傳播現象 |  | R107=27.9% ~ 34.8% | 10-36-熱煙或毒性氣體危害至儲能空間以外 | Impact 54
[7 empty] | R102=19.2% ~ 26.9% |  |  | R109=38.1% ~ 44.0% | P(54)=0.001%
3-6-電芯發生熱失控
|  |  | R095=16.8% ~ 24.8% | [6 empty] | 10-37-熱煙或毒性氣體未危害至儲能空間以外 | Impact 55
[9 empty] | 9-19-消防系統有效發揮冷卻作用 | R112=70.0% ~ 77.3% | P(55)=0.003%
R111=55.4% ~ 61.3%
[10 empty] | 10-38-熱煙或毒性氣體危害至儲能空間以外 | Impact 56
[8 empty] | 8-10-可燃氣體濃度達到LFL |  | R113=22.7% ~ 30.0% | P(56)=0.001%
R110=45.6% ~ 50.8%
[10 empty] | 10-39-熱煙或毒性氣體未危害至儲能空間以外 | Impact 57
[10 empty] | R115=56.0% ~ 61.9% | P(57)=0.001%
9-20-消防系統無法發揮冷卻作用
[9 empty] | R114=38.7% ~ 44.6% | 10-40-熱煙或毒性氣體危害至儲能空間以外 | Impact 58
[5 empty] | 5-11-未發生電芯熱失控傳播現象 | Impact 59 |  |  |  | R116=38.1% ~ 44.0% | P(58)=0.001%
[5 empty] | R118=71.6% ~ 79.1% | P(59)=1.394%
|  |  |  | 4-6-通風排出裝置未啟動 |  | 6-11-未發生模組熱失控傳播現象 | Impact 60 |  |  | 10-41-熱煙或毒性氣體未危害至儲能空間以外 | Impact 62
|  |  |  | R117=64.3% ~ 67.7% |  | R120=73.1% ~ 80.8% | P(60)=0.347% |  | 9-21-消防系統有效發揮冷卻作用 | R126=70.0% ~ 77.3% | P(62)=0.003%
[5 empty] | 5-12-發生電芯熱失控傳播現象 |  | 7-11-未發生電池櫃熱失控傳播現象 | Impact 61 | R125=65.2% ~ 72.1%
| 1-2-值班室或EWCS未通報電池異常 |  |  |  | R119=20.9% ~ 28.4% |  | R122=73.1% ~ 80.8% | P(61)=0.079% |  | 10-42-熱煙或毒性氣體危害至儲能空間以外 | Impact 63
| R092=33.8% ~ 40.1% | [6 empty] | 8-11-可燃氣體濃度未達到LFL |  | R127=22.7% ~ 30.0% | P(63)=0.001%
[6 empty] | 6-12-發生模組熱失控傳播現象 |  | R124=24.6% ~ 27.2%
[6 empty] | R121=19.2% ~ 26.9% |  |  |  | 10-43-熱煙或毒性氣體未危害至儲能空間以外 | Impact 64
[10 empty] | R129=56.0% ~ 61.9% | P(64)=0.001%
9-22-消防系統無法發揮冷卻作用
[7 empty] | 7-12-發生電池櫃熱失控傳播現象 |  | R128=27.9% ~ 34.8% | 10-44-熱煙或毒性氣體危害至儲能空間以外 | Impact 65
[7 empty] | R123=19.2% ~ 26.9% |  |  | R130=38.1% ~ 44.0% | P(65)=0.001%
[10 empty] | 10-45-熱煙或毒性氣體未危害至儲能空間以外 | Impact 66
[9 empty] | 9-23-消防系統有效發揮冷卻作用 | R133=70.0% ~ 77.3% | P(66)=0.008%
R132=55.4% ~ 61.3%
[10 empty] | 10-46-熱煙或毒性氣體危害至儲能空間以外 | Impact 67
[8 empty] | 8-12-可燃氣體濃度達到LFL |  | R134=22.7% ~ 30.0% | P(67)=0.003%
R131=72.8% ~ 75.4%
[10 empty] | 10-47-熱煙或毒性氣體未危害至儲能空間以外 | Impact 68
[10 empty] | R136=56.0% ~ 61.9% | P(68)=0.004%
9-24-消防系統無法發揮冷卻作用
[9 empty] | R135=38.7% ~ 44.6% | 10-48-熱煙或毒性氣體危害至儲能空間以外 | Impact 69
|  |  | 3-7-電芯未發生熱失控 | Impact 70 | 5-13-未發生電芯熱失控傳播現象 | Impact 71 |  |  |  | R137=38.1% ~ 44.0% | P(69)=0.003%
|  |  | R139=22.6% ~ 24.9% | P(70)=5.652% | R142=71.6% ~ 79.1% | P(71)=3.660%
|  |  |  | 4-7-通風排出裝置啟動 |  | 6-13-未發生模組熱失控傳播現象 | Impact 72 |  |  | 10-49-熱煙或毒性氣體未危害至儲能空間以外 | Impact 74
|  |  |  | R141=25.4% ~ 28.1% |  | R144=73.1% ~ 80.8% | P(72)=0.916% |  | 9-25-消防系統有效發揮冷卻作用 | R150=70.0% ~ 77.3% | P(74)=0.017%
[5 empty] | 5-14-發生電芯熱失控傳播現象 |  | 7-13-未發生電池櫃熱失控傳播現象 | Impact 73 | R149=65.2% ~ 72.1%
[5 empty] | R143=20.9% ~ 28.4% |  | R146=73.1% ~ 80.8% | P(73)=0.209% |  | 10-50-熱煙或毒性氣體危害至儲能空間以外 | Impact 75
|  | 2-4-BESS未緊急安全關斷 | [5 empty] | 8-13-可燃氣體濃度未達到LFL |  | R151=22.7% ~ 30.0% | P(75)=0.006%
|  | R138=62.4% ~ 66.0% |  |  |  | 6-14-發生模組熱失控傳播現象 |  | R148=49.2% ~ 54.4%
[6 empty] | R145=19.2% ~ 26.9% |  |  |  | 10-51-熱煙或毒性氣體未危害至儲能空間以外 | Impact 76
[10 empty] | R153=56.0% ~ 61.9% | P(76)=0.006%
9-26-消防系統無法發揮冷卻作用
[9 empty] | R152=27.9% ~ 34.8% | 10-52-熱煙或毒性氣體危害至儲能空間以外 | Impact 77
[7 empty] | 7-14-發生電池櫃熱失控傳播現象 |  |  | R154=38.1% ~ 44.0% | P(77)=0.004%
|  |  | 3-8-電芯發生熱失控 |  |  |  | R147=19.2% ~ 26.9%
|  |  | R140=62.4% ~ 66.0% | [6 empty] | 10-53-熱煙或毒性氣體未危害至儲能空間以外 | Impact 78
[9 empty] | 9-27-消防系統有效發揮冷卻作用 | R157=70.0% ~ 77.3% | P(78)=0.013%
R156=55.4% ~ 61.3%
[10 empty] | 10-54-熱煙或毒性氣體危害至儲能空間以外 | Impact 79
[8 empty] | 8-14-可燃氣體濃度達到LFL |  | R158=22.7% ~ 30.0% | P(79)=0.005%
R155=45.6% ~ 50.8%
[10 empty] | 10-55-熱煙或毒性氣體未危害至儲能空間以外 | Impact 80
[10 empty] | R160=56.0% ~ 61.9% | P(80)=0.007%
9-28消防系統無法發揮冷卻作用
[9 empty] | R159=38.7% ~ 44.6% | 10-56-熱煙或毒性氣體危害至儲能空間以外 | Impact 81
[5 empty] | 5-15-未發生電芯熱失控傳播現象 | Impact 82 |  |  |  | R161=38.1% ~ 44.0% | P(81)=0.005%
[5 empty] | R163=71.6% ~ 79.1% | P(82)=10.041%
|  |  |  | 4-8-通風排出裝置未啟動 |  | 6-15-未發生模組熱失控傳播現象 | Impact 83 |  |  | 10-57-熱煙或毒性氣體未危害至儲能空間以外 | Impact 85
|  |  |  | R162=71.9% ~ 74.6% |  | R165=73.1% ~ 80.8% | P(83)=2.540% |  | 9-29-消防系統有效發揮冷卻作用 | R171=70.0% ~ 77.3% | P(85)=0.045%
[5 empty] | 5-16-發生電芯熱失控傳播現象 |  | 7-15-未發生電池櫃熱失控傳播現象 | Impact 84 | R170=65.2% ~ 72.1%
[5 empty] | R164=20.9% ~ 28.4% |  | R167=73.1% ~ 80.8% | P(84)=0.576% |  | 10-58-熱煙或毒性氣體危害至儲能空間以外 | Impact 86
[8 empty] | 8-15-可燃氣體濃度未達到LFL |  | R172=22.7% ~ 30.0% | P(86)=0.016%
[6 empty] | 6-16-發生模組熱失控傳播現象 |  | R169=24.6% ~ 27.2%
[6 empty] | R166=19.2% ~ 26.9% |  |  |  | 10-59-熱煙或毒性氣體未危害至儲能空間以外 | Impact 87
[10 empty] | R174=56.0% ~ 61.9% | P(87)=0.016%
9-30-消防系統無法發揮冷卻作用
[7 empty] | 7-16-發生電池櫃熱失控傳播現象 |  | R173=27.9% ~ 34.8% | 10-60-熱煙或毒性氣體危害至儲能空間以外 | Impact 88
[7 empty] | R168=19.2% ~ 26.9% |  |  | R175=38.1% ~ 44.0% | P(88)=0.011%
[10 empty] | 10-61-熱煙或毒性氣體未危害至儲能空間以外 | Impact 89
[9 empty] | 9-31-消防系統有效發揮冷卻作用 | R178=70.0% ~ 77.3% | P(89)=0.035%
R177=55.4% ~ 61.3%
[10 empty] | 10-62-熱煙或毒性氣體危害至儲能空間以外 | Impact 90
[8 empty] | 8-16-可燃氣體濃度達到LFL |  | R179=22.7% ~ 30.0% | P(90)=0.013%
R176=72.8% ~ 75.4%
[10 empty] | 10-63-熱煙或毒性氣體未危害至儲能空間以外 | Impact 91
[10 empty] | R181=56.0% ~ 61.9% | P(91)=0.020%
9-32-消防系統無法發揮冷卻作用
[9 empty] | R180=38.7% ~ 44.6% | 10-64-熱煙或毒性氣體危害至儲能空間以外 | Impact 92
[10 empty] | R182=38.1% ~ 44.0% | P(92)=0.014%

## FTA
頂層事件(Top Event )
F1-a1-1(t) | 充電電壓設定不當 | [6 empty] | 電芯內部溫度異常 |  | T1
[7 empty] | F1(t) |  |  |  |  | 電芯溫度或壓力達危險界限FTop(t) The Temperature or Pressure of the Cell Reaches Dangerous Levels
11.1% |  | AND | F1-a1(t) | 充電電壓設定不當 |  | OR |  |  | AND |  | OR
[7 empty] | 0.06943% |  |  | 0.0007601%
1.321%
F1-a1-2(t) | 充電電壓控制器故障 | [5 empty] | F2(t) | 溫度保護機制失效 |  | T2
AND
11.9% | [6 empty] | 1.095% |  |  | 1.29%
[12 empty] | Freq.Ann (Annual Frequency) = | 1.29%
F1-a2-1(t) | 過電壓保護設定不當 | [5 empty] | F2-a1(t) | 電芯內部溫度異常
12.6% |  | AND | F1-a2(t) | 充電電壓設定不當 |  |  | 10.4% |  | AND
1.361%
F1-a2-2(t) | 過電壓保護裝置故障 | [5 empty] | F2-a2(t) | 溫度保護機制失效
10.8% | [6 empty] | 12.4%
F1-b1-1(t) | 充電電流設定不當
10.85% |  | AND | F1-b1(t) | 充電電壓設定不當
1.291%
F1-b1-2(t) | 充電電流控制器故障
AND
11.9%
F1-b2-1(t) | 過電流保護設定不當
12.6% |  | AND | F1-b2(t) | 充電電壓設定不當
1.285%
F1-b2-2(t) | 過電流保護裝置故障
10.2%
F1-c1-1(t) | 充電上限設定不當
10.85% |  | AND | F1-c1(t) | 充電電壓設定不當
1.291%
F1-c1-2(t) | 充電上限控制器故障
AND
11.9%
F1-c2-1(t) | 過充電保護設定不當
12.6% |  | AND | F1-c2(t) | 充電電壓設定不當
1.361%
F1-c2-2(t) | 過充電保護裝置故障
10.8%
F1-d1-1(t) | 充電下限設定不當
10.35% |  | AND | F1-d1(t) | 充電電壓設定不當
1.232%
F1-d1-2(t) | 充電下限控制器故障
AND
11.9%
F1-d2-1(t) | 過放電保護設定不當
13% |  | AND | F1-d2(t) | 充電電壓設定不當
1.404%
F1-d2-2(t) | 過放電保護裝置故障
10.8%
|  |  | F1-e1(t) | 電芯內部電阻異常
11.9%
AND
|  |  | F1-e2(t) | 電池散熱裝置故障
9.2%