## 管網系統參數
喷 头 总 数: | 16
节 点 总 数: | 35
管 段 总 数(含喷头): | 51
防 护 区 底 面 积 （m2）: | 256
海 拔 高 度 （m）: | 0
防 护 区 的 环 境 温 度 （℃）: | 20
95%设计用量的喷放时间 （s）: | 60
外开门弹簧闭门器或弹簧门开口面积 （m2）: | 0
围护结构承受内压的允许压强 （kPa）: | 1.9
储存容器的充压压力 （MPa）: | 20
减压孔板前管网管道容积 （m3）: | 0.1
减压孔板落压比: | 0.52
减压孔板所在的管段号: | 19
设计系数: | 0
减压孔板的结构: | 出口倒角
是否有备用量: | 否
计 算 文 件: | 541.dat

## 防護區域各封閉空間參數
封闭空间号 | 从 | 到 | 封闭空间容 积 (m3) | 非及难燃烧 体容积 (m3) | 设计浓度 (%) | 设计用量 (kg)
1 | 1 | 16 | 1536 | 0 | 40.6 | 1134.04

## 當量管長
管段 号 | 数量 | 型号 | 数量 | 型号 | 数量 | 型号 | 其它当量(m) | 总当量 管长 (m)
17 | 0 |  | 0 |  | 0 |  | 30 | 30
18 | 1 | 变径 20*150 | 1 | 90度弯头- DN150 | 0 |  | 0 | 2.1
19 | 1 | 90度弯头- DN150 | 0 |  | 0 |  | 0 | 2.1
20 | 1 | 90度弯头- DN150 | 0 |  | 0 |  | 0 | 2.1
21 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
22 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
23 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
25 | 1 | 变径 50*65 | 1 | 三通侧通- DN65 | 0 |  | 0 | 7.39
27 | 1 | 变径 50*65 | 1 | 三通侧通- DN65 | 0 |  | 0 | 7.39
29 | 1 | 90度弯头- DN150 | 0 |  | 0 |  | 0 | 2.1
31 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
33 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
35 | 1 | 变径 65*100 | 1 | 三通侧通- DN100 | 0 |  | 0 | 10.82
37 | 1 | 变径 100*150 | 1 | 三通侧通- DN150 | 0 |  | 0 | 12
39 | 1 | 变径 65*100 | 1 | 三通侧通- DN100 | 0 |  | 0 | 10.82
41 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
43 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
44 | 1 | 变径 50*65 | 1 | 三通侧通- DN65 | 0 |  | 0 | 7.39
46 | 1 | 变径 50*65 | 1 | 三通侧通- DN65 | 0 |  | 0 | 7.39
48 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52
50 | 1 | 变径 32*50 | 1 | 三通侧通- DN50 | 0 |  | 0 | 6.52

## 簡化管網當量係數表
从 | 到 | 当 量 系 数
17 | 17 | 51

## 洩壓口面積
必需增设的泄压口面积不小于 （m2）: | 0.57

## 孔板數據
孔 板 前 压 力 （MPa）: | 7.4832
孔 板 孔 径 （mm）: | 35.55
孔 板 后 压 力 （MPa）: | 3.8913

## 管材數據表
管材名称 | SCH80
作用范围 | 全部管材

## 管段數據表
管段号 | 节点 1 | 节点 2 | 管长 (m) | 管径 (mm) | 实际内径 (mm) | 容积 (L) | 当量管长 (m) | 高差 (m) | 流量 (kg/s) | 始端压 力 (MPa) | 终端压 力 (MPa)
17 | 0 | 18 | 1 | 20 | 18.8 5 | 0.279 | 30 | 1 | 0.35 | 7.7433 | 7.4869
18 | 18 | 17 | 2 | 150 | 146. 34 | 33.639 | 2.1 | 0 | 17.96 | 7.4869 | 7.4832
19 | 17 | 20 | 6 | 150 | 146. 34 | 100.918 | 2.1 | 6 | 17.96 | 7.4832 | 3.8913
20 | 19 | 20 | 7.1 | 150 | 146. 34 | 119.419 | 2.1 | 0 | 17.96 | 4.8042 | 3.8913
22 | 23 | 2 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
24 | 26 | 4 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
26 | 22 | 23 | 2 | 50 | 49.2 4 | 3.809 | 7.39 | 0 | 2.24 | 4.6746 | 4.6362
28 | 25 | 26 | 2 | 50 | 49.2 4 | 3.809 | 7.39 | 0 | 2.24 | 4.6746 | 4.6362
30 | 21 | 5 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
32 | 24 | 7 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
34 | 27 | 22 | 4 | 65 | 59 | 10.936 | 10.8 2 | 0 | 4.49 | 4.7666 | 4.6746
36 | 28 | 27 | 4 | 100 | 97.1 8 | 29.669 | 12 | 0 | 8.98 | 4.7958 | 4.7666
38 | 27 | 31 | 4 | 65 | 59 | 10.936 | 10.8 2 | 0 | 4.49 | 4.7666 | 4.6746
40 | 30 | 9 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
41 | 32 | 10 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
43 | 35 | 12 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
45 | 31 | 32 | 2 | 50 | 49.2 4 | 3.809 | 7.39 | 0 | 2.24 | 4.6746 | 4.6362
47 | 34 | 35 | 2 | 50 | 49.2 4 | 3.809 | 7.39 | 0 | 2.24 | 4.6746 | 4.6362
49 | 32 | 14 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585
51 | 35 | 16 | 2 | 32 | 32.4 6 | 1.655 | 6.52 | 0 | 1.12 | 4.6362 | 4.5585

## 噴頭參數表
喷头号 | 喷头入口压力 (MPa) | 喷头流量 (Kg/s) | 等效孔口面积 (cm2) | 实用喷头规格代 号
1 | 4.5585 | 1.12 | 0.94 | 14
2 | 4.5585 | 1.12 | 0.94 | 14
3 | 4.5585 | 1.12 | 0.94 | 14
4 | 4.5585 | 1.12 | 0.94 | 14
5 | 4.5585 | 1.12 | 0.94 | 14
6 | 4.5585 | 1.12 | 0.94 | 14
7 | 4.5585 | 1.12 | 0.94 | 14
8 | 4.5585 | 1.12 | 0.94 | 14
9 | 4.5585 | 1.12 | 0.94 | 14
10 | 4.5585 | 1.12 | 0.94 | 14
11 | 4.5585 | 1.12 | 0.94 | 14
12 | 4.5585 | 1.12 | 0.94 | 14
13 | 4.5585 | 1.12 | 0.94 | 14
14 | 4.5585 | 1.12 | 0.94 | 14
16 | 4.5585 | 1.12 | 0.94 | 14

## IG541用量及儲存容器數據表
设 计 用 量 （kg）: | 1134.04
系 统 剩 余 量 （kg）: | 12.31
总 需 求 量 （kg）: | 1146.36
单 个 储 存 容 器 的 容 积 （L）: | 80
每 瓶 储 药 量 （kg）: | 22.48
充 装 率 （kg/m3）: | 281.06
基 本 储 存 容 器 数 量: | 51
总储存量 （kg）: | 1146.72
备 用 储 存 容 器 数 量: | 0
备用储存量 （kg）: | 0
实 际 喷 射 浓 度 （%）: | 40.94

## Worksheet
Note：
According to the calculations: The calculation is based on NFPA 2001- - Standard on Clean Agent Fire Extinguishing Systems
Total Flooding Quantity. W  K  V  ln( 100 ) S 100  C 1 where: W = volume of inert gas added at standard conditions of 14.7 psia, 70°F (1.013 bar, 21°C) per volume of hazard space [ft3/ft3 (m3/m3)] V = specific volume of inert gas agent at 70°F (21°C) and 14.7 psia (1.013 bar) s = specific volume of inert gas at 1 atmosphere and temperature, t [ft3/ lb (m3/kg)] s = 0.65799 + 0.00239t t = minimum anticipated temperature of the protected volume [°F (°C)] C 1 = inert gas design concentration [volume percent]
IG-541CAD V2.0 Software Copyright (c) Megdragon Software Development Co.,Ltd Tel:(086-022)85689438 Email:megdragon@163.com http://www.megdragon.com